Using Modscan on the DeapSea controllers

Refer to CEPR0019

On page 24 Modbus registers Defined: Note 1 register address =number*256+register offset. Page 4 is for Basic instrumentation. 256*4=1024. This starts out with looking at register 1024. Need an offset of 1.

Using Modscan looking at register 1025 will equal register offset 0 for oil pressure. Register 1026 will be coolant temp. ect